# Innovate UK Innovation Voucher project – Development of a Low Energy 3 Bedroom Prototype Dwelling

# Professor David Johnston, Centre for the Built Environment (CeBE) Group, Leeds Beckett University

# Matthew Brooke-Peat, Centre for the Built Environment (CeBE) Group, Leeds Beckett University

# Dr Jim Parker, Centre for the Built Environment (CeBE) Group, Leeds Beckett University

# June 2015

TABLE OF CONTENTS

Introduction	3

The low energy prototype dwelling	3

Thermal bridging calculations	5

Test method	5

Limitations	6

Results	6

Dynamic thermal simulations	7

Test method	7

Limitations	10

Results	11

Conclusions and recommendations	16

References	17

# Introduction

This report presents the results of the thermal bridging calculations and dynamic thermal simulations that were undertaken to assess the thermal performance of a prototype Code for Sustainable Homes (CSH) Level 6 low energy dwelling that has been designed to have very high levels of building fabric thermal performance and very low energy demand. The calculations were undertaken by the Centre for the Built Environment (CeBE) Group within the Leeds Sustainability Institute at Leeds Beckett University as part of a collaborative project with the dwellings designer Walker Associates. The project was supported by an Innovate UK Innovation Voucher.

The calculations and simulations were performed on the prototype dwelling for Walker Associates in order to test the initial design concept for the prototype dwelling prior to the development and construction of a prototype dwelling which could subsequently be tested and verified prior to marketing within the UK residential market.

## The low energy prototype dwelling

The study dwelling is a 118.5m2 3 storey two/ three bedroom detached property which has a novel spherical architectural form and is elevated above the surrounding ground level (see Figure 1). Consequently access to the dwelling is gained via an elevated decking area that surrounds half of the floor plan of the dwelling. A spherical form was chosen for the dwelling by the designer as a sphere has a smaller surface area-to-volume ratio than any other shape for a given volume. The smaller the surface area-to-volume ratio, then the more thermally efficient the building is for a given level of building fabric performance. As part of the original concept design, the spherical form was elevated above the ground level to enable the dwelling to rotate horizontally in order to track the sun and maximise the collection of solar radiation.

Figure 1 South elevation of the prototype dwelling (Source: Walker Associates, 2015).

Internally, the prototype dwelling comprises an entrance lobby, storage cupboards, a bedroom, shower room, WC, landing and stairs on the entrance level (level 3). On the first floor, (level 5) there is a hallway, an open plan living, kitchen and dining area, a study/bedroom 3 and the stairs to the second floor. Finally, on the second floor (level 6), there is a landing, master bedroom and an en-suite. The internal layout the prototype dwelling is illustrated in Figure 2.

Figure 2 Prototype dwelling layout (Source: Walker Associates, 2015).

The external walls, roof and floor of the prototype dwelling are to be constructed from Structurally Insulated Panels (SIP’s) comprising a 300mm Expanded Polystyrene (EPS) insulated core. The windows and roof light are to be double glazed units in timber frames which are set back within the SIP panel system. To enable a flush external finish to be achieved, all of the windows and the roof lights are to be secondary glazed.

A summary of the U-values for the various elements of the building fabric are contained within Table 1.These figures have been obtained from the as-built SAP worksheet dated 11th August 2011.

| - Element | - U-value (W/m2K) |
| --- | --- |
| - External walls | - 0.12 |
| - Floor | - 0.12 |
| - Roof | - 0.12 |
| - Windows, roof light and door | - 1.00 |

Table 1 U-values of the main elements of the prototype dwelling.

In terms of airtightness, the design air permeability target for the test dwelling is 3.0 m3.h-1.m-2 @ 50Pa. This target is commensurate with the use of an MEV or MVHR system.

# Thermal bridging calculations

A number of thermal bridging calculations were undertaken on the prototype design of the dwelling to assess and quantify the thermal bridging and determine whether there were any potential condensation risks associated with the prototype design. An analysis of the drawings for the prototype design identified a total of 16 No. junctions that were required to be modelled for thermal bridging calculation purposes. These junctions are identified below.

  - Panel Joint.

  - Jamb.

  - Ground Floor with Joist Parallel.

  - Ground Floor with Joists Perpendicular.

  - Intermediate Floor with Joists Parallel.

  - Intermediate Floor with Joists Perpendicular.

  - Partition/External Wall.

  - Service Penetration.

  - Roof Window.

  - Lobby Jamb Top.

  - Lobby Jamb Middle.

  - Lobby Jamb Bottom.

  - Lobby Threshold at Door.

  - Lobby Head.

  - Lobby Threshold at Shell.

  - Lobby Floor/External Wall.

Thermal bridging calculations were performed for all 16 junctions identified above to ascertain the linear thermal transmittance (Ψ-value) and minimum temperature factor (ƒRsi) of each.

## Test method

In order to undertake the thermal bridging calculations, a numerical modelling technique known as thermal modelling was employed. All of the individual thermal bridges associated with each junction type within the prototype dwelling were explicitly thermally modelled using the Physibel TRISCO version 12.0w software program (Physibel, 2010). When undertaking the modelling, the conventions given in BR 497 (Ward & Sanders, 2007) were followed throughout. The equivalent thermal conductivities for all air spaces and voids were calculated in accordance with BS EN ISO 6946 (British Standards Institution (BSI), 2007). Material conductivities were sourced from manufacturers’ literature where possible based on the project specification. In instances where these could not be obtained, suitable values were sourced from BS EN 12524 (BSI, 2000) or from BR 443 (Anderson, 2006). The geometry of the thermally modelled junctions was based on the content of the design drawings provided to the CeBE Group at Leeds Beckett University by Walker Associates.

## Limitations

The complex geometry of the spherical envelope had to be simplified to enable thermal modelling of the junctions. The rectilinear nature of the thermal modelling software meant that the number of nodes that would be created in the model when attempting to represent the curved nature of the building envelope would exceed the software’s processing capability. Consequently, a simplified rectilinear representation of the building envelope was formed in the thermal models with each of the flanking elements to the junction represented in a single plane (flattened). The locations where the geometry of the curved envelope has the maximum influence are at the floor junctions. In order to calculate results that are representative of the thermal bridging inherent to the design, the angle of intersection between the floors and the simplified rectilinear representation of the building envelope matched the average intersection angles with the curved envelope. This approach is considered to have minimal impact on the accuracy of the results because the additional length of the flanking element that would be generated by the curved envelope would be very small at the junctions.

The elevated position of the spherical envelope meant that the ground floor is considered similar to an exposed upper floor in construction but had to be represented as an intermediate floor in the thermal models. However, the boundary conditions below the floor structure were for a downward heat flow. The thermal bridging equation applied to the ground floor was based on the equation for an intermediate floor from BR 497 (Ward & Sanders, 2007).

The proposed design shows secondary glazing to the window and roof window openings. In order to model this arrangement, two adiabatic boundaries were incorporated into the thermal models to represent the two glazing units.

## Results

The results of the thermal bridging calculations are presented for each junction detail in Appendix A. A summary of these results is also presented in Table 2 for ease of reference. The columns headed Ψ and ƒRsi are the values calculated for the design. The values in the column headed ADD Ψ represent the Approved Design Detail (Approved) values identified in Appendix K of SAP 2012 (Department of Energy and Climate Change (DECC), 2013). The values in the column headed Default Ψ represent the Building Regulations Default values identified in Appendix K of SAP 2012 (ibid).

As can be seen from Table 3, the Ψ-values calculated for the jamb, ground floor and particularly the intermediate floor junctions improve upon the Approved and Default values for each of the junctions. At the time of writing there is no Approved value identified within Appendix K of SAP 2012 for a roof window, but the calculated value improves upon the Default value listed in Appendix K of SAP 2012 (DECC, 2013). There are also no Approved or Default values for the other junctions thermally modelled as part of the project.

In comparison, the Ψ-values calculated for the door threshold junction to the lobby and the lobby wall/floor junction are considered to be high at 0.348 W/m·K and 0.411 W/m·K, respectively. The reason for the high Ψ-value for the door threshold junction to the lobby is a consequence of the brush seal that penetrates through the floor insulation, resulting in a discontinuity in the insulation layer at this junction. It would be possible to revise the junction design to provide continuity of the insulation across the threshold. This could be achieved by providing a brush seal with an insulated casing or alternatively, by reposition the brush seal outside of the thermal envelope. The reason for the high Ψ-value for the lobby/wall floor junction (0.411 W/m·K) can be attributed to the position of the brush seal coupled with the fact that the structural steelwork fully penetrates the thermal envelope. It would be possible to revise this junction to provide continuity of the insulation layer by limiting the number and amount of penetrations through the insulation layers.

In terms of surface temperature factors, the position of the glazing in the proposed jamb junction creates an internal surface temperature (Tsi) of 15° under the modelled conditions. This results in a ƒRsi of 0.750 that is equal to the critical temperature factor (ƒCRsi) of 0.750 (Ward, 2006). Although the ƒRsi of the jamb junction does comply with Part L of the Building Regulations for England (HM Government, 2013), there is no margin of safety. It is understood that the jamb detail will be used for the head and sill junctions of the window openings. Improvements could be made to the position of the primary glazing unit by squaring off its edges. In addition, thermal modelling of the proposed services penetration through the floor of the prototype dwelling junction resulted in a Tsi of 13.43° under modelled conditions producing a ƒRsi of 0.672 to the stainless steel part of the spigot. This is below the ƒCRsi of 0.750 (Ward, 2006) and presents a risk of surface condensation. The design of the spigot could be revised to eliminate this risk.

| Junction: | Ref: | Ψ: | ƒRsi | ADD Ψ: | Default Ψ: |
| --- | --- | --- | --- | --- | --- |
| Panel Joint | TB/01 | 0.004 | 0.983 | NA | NA |
| Jamb | TB/02 | 0.038 | 0.750 | 0.050 | 0.100 |
| Ground Floor with Joist Parallel | TB/03 | 0.019 | 0.971 | 0.070 | 0.140 |
| Ground Floor with Joists Perpendicular | TB/04 | 0.062 | 0.970 | 0.070 | 0.140 |
| Intermediate Floor with Joists Parallel | TB/05 | -0.001 | 0.980 | 0.070 | 0.140 |
| Intermediate Floor with Joists Perpendicular | TB/06 | -0.001 | 0.979 | 0.070 | 0.140 |
| Partition/External Wall | TB/07 | 0.000 | 0.979 | NA | NA |
| Service Penetration | TB/08 | 0.091 | 0.672 | NA | NA |
| Roof Window | TB/09 | 0.031 | 0.874 | NA | 0.060 |
| Lobby Jamb Top | TB/10 | 0.003 | 0.925 | NA | NA |
| Lobby Jamb Middle | TB/11 | 0.011 | 0.852 | NA | NA |
| Lobby Jamb Bottom | TB/12 | 0.011 | 0.852 | NA | NA |
| Lobby Threshold at Door | TB/13 | 0.348 | 0.809 | NA | NA |
| Lobby Head | TB/14 | 0.000 | 0.932 | NA | NA |
| Lobby Threshold at Shell | TB/15 | 0.068 | 0.963 | NA | NA |
| Lobby Floor/External Wall | TB/16 | 0.411 | 0.842 | NA | NA |

Table 2 Summary of thermal bridging calculation results.

# Dynamic thermal simulations

As part of the Innovate UK Innovation Voucher, two baseline dynamic thermal simulations were undertaken on the prototype dwelling in order to estimate the dwelling’s total energy consumption and determine whether there would be a risk of summertime overheating.

In both of these simulations it has been assumed that all of the space and domestic hot water heating for dwelling was provided by a gas-fired condensing combination boiler and that the dwelling was mechanically ventilated using an MVHR system. In one of the simulations, a ‘normal’ 9am to 5pm working week day occupancy regime has been assumed (scenario 1.1) whilst on the other simulation a home working week day occupancy regime has been assumed (scenario 1.2). In addition, as the original concept design involved rotating the dwelling horizontally to maximise the collection of solar radiation, both scenarios have been modelled with the building rotated at 30° increments. This has been undertaken to establish if there are any energy benefits or penalties associated with rotating the building.

## Test method

The dynamic thermal simulations (DTS) have been undertaken using Integrated Environmental Solutions (IES) Virtual Environment (VE) software version 2014.2.1.0 (IES, 2014). This software is approved for regulatory compliance energy calculations for non-domestic buildings. Simulations can be produced at hourly time-steps covering 8,760 hours of operation (all 365 days of the year). The IES software is validated for use against various global standards, the most prominent of these being the Chartered Institute of Building Services Engineers (CIBSE) “TM33: Tests for Software Accreditation & Verification” in the UK and the American Society of Heating, Refrigeration and Air Conditioning Engineers (ASHRAE) “Standard 140-2007: Standard method of test for the evaluation of building energy analysis computer programs” (CIBSE, 2006a; ASHRAE, 2007).

Two simulation weather files for the Leeds area have been used for this analysis; the CIBSE Test Reference Year (TRY) and Design Summer Year (DSY). These files were chosen for two reasons. First of all, they are approved for use in non-domestic building Part L regulatory compliance calculations (CIBSE, 2006b). Secondly, they are the closest approved weather files that are available to the proposed location of the prototype dwelling. The TRY files are used to estimate annual energy and thermal performance, whilst the DSY files are used to evaluate summer overheating. The TRY files are created using actual weather data from a twenty year period, with the most average month for each month being incorporated within the simulation file. A similar method is used for the DSY files, but these are based upon the hottest months from the data set covering the period April – September inclusive. The DSY file is used to simulate heat wave conditions

The model geometry is based upon the drawings provided by the client shown in Figure 2. Unfortunately, it is not possible to produce a fully curved sphere using the IES VE software. Consequently, a fully faceted sphere has been used to represent the geometry of the prototype dwelling. The resultant geometry used in the IES VE software is visualised in Figure 3.

Figure 3 Example image of the geometry used in the DTS models.

There are five main zone types used in the model which use shared thermal templates. The contents of these templates are described in the following paragraphs. The five zone types are: bathrooms, bedrooms, circulation space, kitchen and lounge (also used for the study).

Internal heat gains and the associated operating schedules are based upon those specified in the National Calculation Methodology (NCM) database for domestic occupancy. The NCM underpins the calculation method used in both SAP and the non-domestic alternative. The occupancy schedules for scenario 1 are illustrated in Figure 4. The heating schedules have also been assumed to follow these occupancy patterns. As the NCM input data is meant for use in much larger non-domestic buildings, an occupant density of 4m2/person is normally used. However, this would be unrealistic in this instance. It has therefore been assumed that one person would be in each space for a fraction of the occupied hours as per the schedule shown in Figure 4. It should be noted that when using a ‘fraction’ of a person this merely relates to them being in the space for some of the hour and not for example half a person in the room for a full hour. In the model, people are represented as a heat gain. It is assumed that all occupants are adults and account for 70 W/m2 of sensible and 70 W/m2 of latent heat gain.

Figure 4 Occupancy schedules used in the thermal analysis.

Other internal heat gains come from equipment and lighting. These also operate on the same schedules as the occupancy shown in Figure 4. There are however different standard lighting levels and different types of equipment installed within each space, resulting in different levels of internal heat gains. A summary of the heat gains associated with each zone type is contained within Table 3. The lighting heat gains are based upon default NCM values for low-energy lighting. The model used for scenario 1.2 uses identical heat gain inputs but has occupancy, equipment and lighting operations beginning at 10:00am in both the lounge and study areas.

|  | Equipment W/m2 | Lighting W/m2/(100lux) | Lux level |
| --- | --- | --- | --- |
| Bathrooms | 1.67 | 5.20 | 150 |
| Bedrooms | 3.58 | 5.20 | 100 |
| Circulation | 1.57 | 5.20 | 100 |
| Kitchen | 30.28 | 5.20 | 300 |
| Lounge/Study | 3.90 | 5.20 | 150 |

Table 3 Summary of equipment and lighting internal heat gain inputs.

All of the models have the same fabric and HVAC inputs. The U-values for the building fabric have been obtained from the as-built SAP worksheet dated 11th August 2011 (shown in Table 1), with an adjustment made for thermal bridging based upon a calculated y-value of 0.023. The y-value is based upon the findings of the thermal bridging calculations discussed earlier. A gas combination boiler with a seasonal efficiency of 89% has been used in the models as the sole heat source for both space and domestic hot water heating. A heating set point of 21°C (internal temperature) and a cooling set point (the point at which free cooling is provided through bypass of the heat recovery system) of 25°C (internal temperature) has been assumed in the models. The heat recovery system is assumed to have a thermal efficiency of 90%. The balanced MVHR system is assumed to operate continuously delivering 0.5 air changes per hour in all spaces with extracts in the kitchen and bathroom areas. A specific fan power of 0.46 Watts per litre per second (W/l/s) has been used in accordance with the original SAP worksheets provided by the client (Golinski, 2011). Air exchanges that are a result of infiltration are also referenced from the SAP worksheet and are assumed to provide 0.17 air changes per hour throughout the dwelling.

Results analysis is based upon total annual energy consumption for space heating, domestic hot water, ventilation system energy (referred to as ‘ventilation’ in the results), lighting and equipment. Overheating has been evaluated using two different metrics. Under traditional measures of overheating used for non-domestic buildings, a room is considered to provide uncomfortable conditions when the internal temperature exceeds 25°C for more than 5% of the occupied hours and exceeds 28°C for more than 1% of the occupied hours (CIBSE, 2006c). This is a more rigorous test of potential overheating than is currently used for domestic buildings in SAP. It has been assumed that external shutters will be closed during all daylight hours in the overheating analysis. This is again in accordance with specifications set within the SAP calculations provided by the client (Golinski, 2011).

The absolute metrics used to assess overheating mentioned above were superseded in 2013 in favour of adaptable comfort metrics. The finite metrics were defined in the CIBSE Guide A document (CIBSE, 2006c) but have been updated to align with other European and American metrics. The justification for this and the calculation methods are defined in the document “TM52: The limits of thermal comfort: avoiding overheating in European buildings” (CIBSE, 2013). This sets out three criteria to evaluate overheating based upon the theory of adaptive comfort, which acknowledges that people are more tolerant of higher internal temperatures when external temperatures are higher themselves. Both assessment methods have been used here to provide a comparison. The absolute metrics help to illustrate the actual temperatures that will be experienced in the dwelling, whereas the adaptive comfort metrics provide a more holistic illustration of personal thermal comfort.

The adaptable comfort metrics measure: hours of exceedence; the daily weighted exceedence; and the upper limit temperature. These are defined below:

  - Hours of exceedance – Sets a limit for the number of hours that the operative temperature can exceed the threshold comfort temperature (upper limit of the range of comfort temperature) by one degree or more during the occupied hours of a typical non-heating season (1st May to the 30th September). The number of hours during which the difference between internal and external temperatures (ΔT – Delta T) is greater than or equal to one degree (K) during the period May to September inclusive, shall not be more than 3% of occupied hours.

  - Daily weighted exceedance – Deals with the severity of overheating, which can be as important as its frequency, the level of which is a function of both temperature rise and its duration. This criterion sets a daily limit for acceptability. To allow for the severity of overheating, the weighted exceedence shall be less than or equal to six in any one day.

  - Upper limit temperature – Sets an absolute maximum daily temperature for a room, beyond which the level of overheating is unacceptable. It sets an absolute maximum value for the indoor operative temperature; the value of ΔT shall not exceed 4K.

## Limitations

It is important to note that the DTS models used here are not approved for regulatory compliance calculations for dwellings; they are only approved for regulatory compliance use in non-domestic buildings. This also applies to the weather files used in the simulation. This type of modelling does enable a much more detailed energy and thermal performance analysis to be undertaken than would otherwise be the case if a SAP calculation was used. This is particularly relevant to the overheating analysis included in this report.

As mentioned previously, there are limitations associated with replicating the geometry of the prototype dwelling within the modelling software. As such, a faceted, rather than perfect sphere, has been constructed within the model. However, this does not result in any additional thermal bridging, as this value is defined independently of the geometry in this type of model.

The software used as part of this analysis has limited scope for the assessment of renewable energy generation. In this instance, the potential for photovoltaic (PV) panels and wind turbines has been evaluated. The way in which these technologies are modelled in the DTS software is relatively simple. There is no specific function for mounting these technologies on the building in the model space. Inputs are limited to the size of the respective systems, their orientation, inclination (in the case of PV) and height (in the case of wind turbines).

## Results

- Annual energy consumption and heating load

Energy performance results from the annual simulation for scenarios 1.1 and 1.2 are presented in Figure 5. These charts include total consumption, space heating and hot water, ventilation, lighting and equipment. The space heating and hot water values have been combined in Figure 5 as the space heating value in isolation is too low to be visualised at this scale. The chart illustrates results for each iteration of the model at 30° increments. Additional charts have been included in Figure 6 to illustrate space heating consumption only, again at 30° increments.

- (a) Scenario 1.1: annual kWh consumed.

- (b) Scenario 1.2: annual kWh consumed.

Figure 5 Total and end-use annual energy consumption at 30° increments.

- (a) Scenario 1.1: annual space heating kWh consumed.

- (b) Scenario 1.2: annual space heating kWh consumed.

Figure 6 Total and end-use annual energy consumption at 30° increments.

As can be seen from Figure 5 and 6, the rotation of the dwelling has a relatively small impact on total energy consumption and the amount of energy required for space heating. It is in fact only space heating energy consumption that changes between each iteration, as this is the only orientation dependant variable. The results indicate that there is a total of 75.5 kWh/annum difference in scenario 1.1 and 81 kWh/annum in scenario 1.2 between the best performing (0°) and worst performing orientation (210°). The total energy consumption differs only slightly between scenarios 1.1 and 1.2 with a mean difference of 82 kWh/annum for all orientations of the models.

Unheated storage voids are included in the design of the dwelling and these effectively act as buffer zones in terms of heat loss. These have not been included in the conditioned floor area of the DTS model which is equal to 127.64m2. Using this area, the total mean energy consumption of the baseline SAP dwelling for all orientations in scenario 1.1 is 113.96 kWh/m2/year of which 19.11 kWh/m2/year is consumed through space heating. The maximum consumption is at an orientation of 210° and is estimated at 114.23 kWh/m2/year (19.37 kWh/m2/year space heating); the minimum is at 0° and is estimated at 113.64 kWh/m2/year (18.78 kWh/m2/year space heating).

The total mean energy consumption of the dwelling for all orientations in scenario 1.2 is 122.75 kWh/m2/year of which 18.71 kWh/m2/year is consumed through space heating. The maximum consumption is at an orientation of 210° and is estimated at 123.04 kWh/m2/year (18.99 kWh/m2/year space heating); the minimum is at 0° and is estimated at 122.40 kWh/m2/year (18.35 kWh/m2/year space heating). The longer periods of occupancy and consumption from equipment and lighting result in an increase in the overall energy use in scenario 1.2. However, the energy use attributable to space heating is reduced slightly, despite the extended periods during which space heating is required, due to the increased internal heat gains.

- Overheating

The potential for overheating has been evaluated using the metrics described in paragraphs 28 and 39 using the Leeds DSY simulation weather file. Although overheating can be assessed in all of the rooms within the prototype dwelling, this analysis focuses only on those rooms with the highest levels of occupancy, namely: L3 Bedroom, L6 Bedroom, L5 Study, L5 Lounge and L5 Kitchen. Cooling is provided by a summertime bypass incorporated within the MVHR system which operates only when the internal temperature reaches 25°C. It is also assumed that the external shutters are closed during daylight hours as per the SAP worksheet dated 11th August 2011. Table 4 and Table 5 present the results for the overheating analysis under the absolute metric for scenarios 1.1 and 2.1 respectively, whilst Table 6 and Table 7 present the overheating analysis results using the adaptive comfort metrics. In all of the tables, cells shaded in red indicate a fail case. For the adaptive comfort metrics, a room is considered to have failed if two out of the three criteria are failed.

Table 4 Predicted overheating for scenario 1.1 using absolute metrics.

Table 5 Predicted overheating for scenario 1.2 using absolute metrics.

Table 6 Predicted overheating for scenario 1.1 using adaptive comfort metrics.

Table 7 Predicted overheating for scenario 1.2 using adaptive comfort metrics.

As can be seen in Table 4 and Table 5, all of the selected rooms in the dwelling exceed the thresholds for the percentage of occupied hours in both scenarios using the absolute metrics. Overheating is particularly pronounced in the study, lounge and kitchen with a large percentage of hours exceeding the thresholds in all cases.

When evaluated using the adaptive comfort metrics, the results are less severe. The L3 bedroom is not considered to overheat in either scenario in any orientation. In scenario 1.1, the L6 bedroom passes in all orientations and only fails when orientated between 0° – 90° in scenario 1.2. Although the overheating is perceived to be less severe for the study, lounge and kitchen when measured using the adaptive comfort criteria, these spaces are still considered to overheat to an unacceptable level, as they fail two out of the three criteria in all cases.

- Renewable energy generation

The potential for renewable energy sources to provide enough electricity to power the dwelling for one year has been assessed as part of this work. The limitations described in paragraph 32 restrict the scope of this analysis. It should also be noted that energy generated through the renewable systems would only mean that the building used zero net energy, as electricity generated on site could not necessarily be used at the time of production. It is likely that the majority of it would need to be exported to the national grid at the time of generation. Without some form of energy storage system, it would not be possible for the building to operate autonomously in terms of electricity. The maximum electricity required by the baseline SAP model (scenario 1.1) has been used as the target generation value in this instance; this is equal to 14,580 kWh. The amount of electricity generated has not been optimised to meet this exact amount; the simulated arrays were simply adjusted at 5m2 increments to most closely match the 14,580 kWh baseline.

There are four different types of PV generation systems that can be modelled using the DTS software. These include Amorphous silicon, Monocrystaline silicon, ‘other thin films’ and polycrystalline systems. Results for each system type are shown below in Table 8. They have been ranked from the smallest to the largest array required. All systems are assumed to be south facing (at an orientation of 180°) and to be at an inclination of 30° so that they are optimised for summer time collection. It is also assumed that there is no over-shading. As L6 of the dwelling (the top floor) has a surface area of approximately 49m2, it is very unlikely that a building mounted PV system could produce enough electricity to offset the total electricity consumed in one year.

| - System: | - Size (m2) | - Energy generated (kWh): |
| --- | --- | --- |
| - Monocrystaline silicon | - 155 | - 15,014 |
| - Polycrystaline silicon | - 180 | - 14,753 |
| - Other thin films | - 280 | - 14,863 |
| - Amorphous silicon | - 400 | - 14,862 |

Table 8 Estimated electricity generated by alternative PV systems.

The size and type of wind turbine that could accompany the building will be highly dependent on planning restriction in specific areas, so the following results should be seen as being indicative only. The potential to generate power will also be highly dependent on the local topography, the exposure of the site and the form and layout of the built environment that surrounds the site. It is assumed in this exercise that the dwelling is in an unsheltered position.

Three hub heights have been simulated; these were set at 10m, 15m and 20m from the ground level. The power rating (kW) required at each height to generate sufficient electricity and the totals generated in one year are shown in Table 9. As with the PV systems, these have not been optimised to match the electricity demand and have been increased in capacity at increments of 5 kW until enough electricity is generated to serve the dwelling for one year. This most relevant wind turbine would be the version with a 10m hub height, which would generate 14,334 kWh at a rating of 45kW, just under the baseline electricity demand.

| - Hub height (m) | - Power rating (kW) | - Energy generated (kWh): |
| --- | --- | --- |
| - 10 | - 50 | - 15,926 |
| 15 | - 35 | - 14,583 |
| 20 | - 30 | - 14,978 |

Table 9 Estimated electricity generated by alternative PV systems.

# Conclusions and recommendations

The following conclusions can be drawn from the findings of the thermal bridging calculations:

  - The majority of the junction designs that were thermally modelled performed well in terms of the extent of thermal bridging and risk of condensation and mould growth.

  - The jamb junction modelled achieves regulatory compliance but the ƒRsi is equal to the ƒCRsi.  The design of the jamb junction could be improved to increase the temperature factor and provide a more comfortable margin.

  - The services penetration that was thermally modelled presents a risk of condensation. The spigot could be redesigned to thermally isolate the stainless steel element or remove it entirely to eliminate the condensation risk.

  - The penetration of the lobby floor insulation layer by a brush seal at the lobby door threshold creates an excessive thermal bridge. The junction design could be revised to provide continuity of insulation.

  - The lobby floor/external wall junction was found to have high degree of thermal bridging.  The extent of thermal bridging is a consequence of structural steel and a brush seal penetrating the insulation layers. The junction could be redesigned to reduce the extent of thermal bridging.

The following conclusions can be drawn from the findings of the dynamic thermal simulation calculations:

  - Rotating the building has a limited impact on its thermal performance. There is a difference of only 76 kWh/annum in scenario 1.1 and 81 kWh/annum in scenario 1.2 between the best and worst performing orientations of the dwelling. The building is at its most efficient when orientated at 0° and at its least efficient when orientated at 210°. It should be noted that a rotation greater than 180° would be required to cover this range.

  - The space heating of the dwelling for the conditioned floor area is very low with a load of approximately 16 kWh/m2 per annum which is close to the Passivhaus target of 15 kWh/m2 for space heating.

  - Significant overheating would be experienced within the dwelling using the specification tested in this work. The summer bypass feature of the MVHR system will not provide enough fresh air to mitigate overheating in either scenario 1.1 or 1.2.

  - Although the dwelling performs slightly better when using the adaptive comfort criteria to assess overheating, temperatures would still exceed acceptable levels, particularly in the spaces with the longest periods of occupancy (lounge, study and kitchen).

  - Electricity demand could be met by either PV or a wind turbine installed on site, although the software used for this analysis has limited scope for evaluating these systems in detail. The systems tested here would represent large installations that would have to mounted remotely from the building.

The following recommendations are made based on the conclusions of the thermal bridging calculations:

  - The jamb junction should be revised to increase the internal surface temperature and further reduce the risk of condensation and mould growth.  This could be achieved by squaring the edges of the glazing units.

  - The spigot for the services penetration should be redesigned to eliminate the risk of condensation by isolating the stainless steel element or removing it entirely.

  - The lobby door threshold junction design should be revised to provide continuity of insulation.  This will require the brush seal to have an insulated casing or be repositioned outside of the insulated envelope.

  - The design of the lobby floor junction with the lobby wall should be revised to provide a greater continuity of insulation.  This could be achieved by reducing the penetration of the insulation with steelwork and brush seal.

The following recommendations are made based on the conclusions of the dynamic thermal simulations calculations:

  - It will be useful to establish how much energy is required to rotate the building. Potential savings from rotation are relatively low and it would only be worth including this feature if the energy required to do this was offset by space heating energy savings.

  - Potential mitigation measures that can significantly reduce overheating need to be investigated, as the scenarios tested here would lead to a very uncomfortable thermal environment during the summer months. These measures could include additional mechanical ventilation, air conditioning or natural ventilation.

  - At present, the window design effectively results in a triple glazed unit. It may not be possible to retain this unit and introduce natural ventilation so alternatives may need to be explored.

  - Simulations included in this report were limited to the Leeds area only; simulations for other areas of the UK will be required to further understand potential performance.

  - Bespoke analysis would help to improve building performance for potential clients with non-standard work schedules.

  - Further evaluation of renewable energy generation technologies is advised using specialist software and localised weather data. The feasibility of wind turbine height and power rating should be considered for built-up areas.

# References

Anderson, B. (2006) Conventions for U-value Calculations. BR 443. Watford: Building Research Establishment.

ASHRAE (2007) Standard 140-2007: Standard method of test for the evaluation of building energy analysis computer programs. Atlanta: ASHRAE.

British Standards Institution (2000) BS EN 12524: Building Materials and Products – Hygrothermal Properties – Tabulated Design Values. Milton Keynes: British Standards Institution.

British Standards Institution. (2007) BS EN ISO 6946: Building Components and Building Elements – Thermal Resistance and Thermal Transmittance – Calculation Methods. Milton Keynes: British Standards Institution.

CIBSE (2006a) TM33: Tests for Software Accreditation & Verification. London: CIBSE.

CIBSE (2006b) Guide A: Environmental Design. CIBSE: London.

CIBSE (2006c) Current CIBSE TRY and DSY Hourly Weather Data (2005 files). London: CIBSE.

CIBSE (2013) TM52: The limits of thermal comfort: avoiding overheating in European buildings. CIBSE: London.

Department of Energy and Climate Change (2013) SAP 2012: The Government’s Standard Assessment Procedure for Energy Rating of Dwellings. Watford: Building Research Establishment.

Golinksi, J. (2011) Regulations compliance report for Eco Dwelling Prototype. Printed 11th August 2011 at 13:21:08.

HM Government (2013) Approved Document L1A: Conservation of Fuel and Power in New Dwellings. The Building Regulations 2010. London: NBS.

Integrated Environmental Solutions. (2014) Virtual Environment, version 2014.2.1.0.

Physibel (2010) TRISCO. version 12.0w [Software]. Maldegem: Physibel.

Walker Associates (2015) Personal Communication, June 2015.

Ward, T. (2006) Assessing the Effects of Thermal Bridging at Junctions and Around Openings. IP 1/06. Watford: Building Research Establishment.

Ward, T. and Sanders, C. (2007) Conventions for Calculating Linear Thermal Transmittance and Temperature Factors. BR 497. Watford: Building Research Establishment.

# Appendix A

# References